## Commands
C_NAME | C_VALUE | C_DEFINE | Command Group | Number | FW | Repeat FW | BW | Name | IEC62386 Version | Description | Notes
|  | //bit8=extended commands, bit9=repeat | Arc power control | － | YAAA AAA0 XXXX XXXX |  | NO | DIRECT ARC POWER CONTROL |  | Adjusts the lighting control level to any level XXXX XXXX according to the Fade time. | 0=OFF, 1-254=LEVEL, 255=MASK (no change)
OFF | 0 | #define DALI_OFF 0 //0 - Turns off lighting. | Arc power control | 0 | YAAA AAA1 0000 0000 |  | NO | OFF |  | Turns off lighting.
UP | 1 | #define DALI_UP 1 //1 - Increases the lighting control level for 200 ms according to the Fade rate. | Arc power control | 1 | YAAA AAA1 0000 0001 |  | NO | UP |  | Increases the lighting control level for 200 ms according to the Fade rate. | The slave does not move from the turn-off state (Actual level = 0) to the turn-on state, or vice versa.
DOWN | 2 | #define DALI_DOWN 2 //2 - Decreases the lighting control level for 200 ms according to the Fade rate. | Arc power control | 2 | YAAA AAA1 0000 0010 |  | NO | DOWN |  | Decreases the lighting control level for 200 ms according to the Fade rate. | The slave does not move from the turn-off state (Actual level = 0) to the turn-on state, or vice versa.
STEP_UP | 3 | #define DALI_STEP_UP 3 //3 - Increments the lighting control level (without fade). | Arc power control | 3 | YAAA AAA1 0000 0011 |  | NO | STEP UP |  | Increments the lighting control level (without fade). | The slave does not move from the turn-off state (Actual level = 0) to the turn-on state, or vice versa.
STEP_DOWN | 4 | #define DALI_STEP_DOWN 4 //4 - Decrements the lighting control level (without fade). | Arc power control | 4 | YAAA AAA1 0000 0100 |  | NO | STEP DOWN |  | Decrements the lighting control level (without fade). | The slave does not move from the turn-off state (Actual level = 0) to the turn-on state, or vice versa.
RECALL_MAX_LEVEL | 5 | #define DALI_RECALL_MAX_LEVEL 5 //5 - Maximizes the lighting control level (without fade). | Arc power control | 5 | YAAA AAA1 0000 0101 |  | NO | RECALL MAX LEVEL |  | Maximizes the lighting control level (without fade). | If the slave is in the turn-off state (Actual Level = 0), it moves to the turn-off state.
RECALL_MIN_LEVEL | 6 | #define DALI_RECALL_MIN_LEVEL 6 //6 - Minimizes the lighting control level (without fade) | Arc power control | 6 | YAAA AAA1 0000 0110 |  | NO | RECALL MIN LEVEL |  | Minimizes the lighting control level (without fade) | If the slave is in the turn-off state (Actual Level = 0), it moves to the turn-off state.
STEP_DOWN_AND_OFF | 7 | #define DALI_STEP_DOWN_AND_OFF 7 //7 - Decrements the lighting control level and turns off lighting if the level is at the minimum (without fade). | Arc power control | 7 | YAAA AAA1 0000 0111 |  | NO | STEP DOWN AND OFF |  | Decrements the lighting control level and turns off lighting if the level is at the minimum (without fade).
ON_AND_STEP_UP | 8 | #define DALI_ON_AND_STEP_UP 8 //8 - Increments the lighting control level and turns on lighting if lighting is off (with fade). | Arc power control | 8 | YAAA AAA1 0000 1000 |  | NO | ON AND STEP UP |  | Increments the lighting control level and turns on lighting if lighting is off (with fade).
ENABLE_DAPC_SEQUENCE | 9 | #define DALI_ENABLE_DAPC_SEQUENCE 9 //9 - It shows the repeat start of the DAPC command. | Arc power control | 9 | YAAA AAA1 0000 1001 |  | NO | ENABLE DAPC SEQUENCE |  | It shows the repeat start of the DAPC command.
GO_TO_LAST_ACTIVE_LEVEL | 10 | #define DALI_GO_TO_LAST_ACTIVE_LEVEL 10 //10 DALI-2 - Adjusts the lighting control level to the last light control level according to the Fade time. (Command that exist only in IEC62386-102ed2.0) | Arc power control | 10 | YAAA AAA1 0000 1010 |  | NO | GO TO LAST ACTIVE LEVEL | DALI-2 | Adjusts the lighting control level to the last light control level according to the Fade time. (Command that exist only in IEC62386-102ed2.0)
RESERVED11 | 11 | #define DALI_RESERVED11 11 //11 - [Reserved] | Arc power control | 11 | YAAA AAA1 0000 11XX |  | NO | RESERVED |  | [Reserved]
RESERVED12 | 12 | #define DALI_RESERVED12 12 //12 - [Reserved] | Arc power control | 12 | YAAA AAA1 0000 11XX |  | NO | RESERVED |  | [Reserved]
RESERVED13 | 13 | #define DALI_RESERVED13 13 //13 - [Reserved] | Arc power control | 13 | YAAA AAA1 0000 11XX |  | NO | RESERVED |  | [Reserved]
RESERVED14 | 14 | #define DALI_RESERVED14 14 //14 - [Reserved] | Arc power control | 14 | YAAA AAA1 0000 11XX |  | NO | RESERVED |  | [Reserved]
RESERVED16 | 16 | #define DALI_RESERVED16 16 //16 - [Reserved] | Arc power control | 16 | YAAA AAA1 0000 11XX |  | NO | RESERVED |  | [Reserved]
GO_TO_SCENE0 | 16 | #define DALI_GO_TO_SCENE0 16 //16 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 16 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE1 | 17 | #define DALI_GO_TO_SCENE1 17 //17 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 17 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE2 | 18 | #define DALI_GO_TO_SCENE2 18 //18 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 18 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE3 | 19 | #define DALI_GO_TO_SCENE3 19 //19 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 19 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE4 | 20 | #define DALI_GO_TO_SCENE4 20 //20 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 20 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE5 | 21 | #define DALI_GO_TO_SCENE5 21 //21 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 21 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE6 | 22 | #define DALI_GO_TO_SCENE6 22 //22 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 22 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE7 | 23 | #define DALI_GO_TO_SCENE7 23 //23 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 23 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE8 | 24 | #define DALI_GO_TO_SCENE8 24 //24 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 24 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE9 | 25 | #define DALI_GO_TO_SCENE9 25 //25 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 25 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE10 | 26 | #define DALI_GO_TO_SCENE10 26 //26 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 26 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE11 | 27 | #define DALI_GO_TO_SCENE11 27 //27 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 27 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE12 | 28 | #define DALI_GO_TO_SCENE12 28 //28 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 28 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE13 | 29 | #define DALI_GO_TO_SCENE13 29 //29 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 29 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE14 | 30 | #define DALI_GO_TO_SCENE14 30 //30 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 30 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
GO_TO_SCENE15 | 31 | #define DALI_GO_TO_SCENE15 31 //31 - Adjusts the lighting control level for Scene XXXX according to the fade time. | Arc power control | 31 | YAAA AAA1 0001 XXXX |  | NO | GO TO SCENE |  | Adjusts the lighting control level for Scene XXXX according to the fade time.
RESET | 544 | #define DALI_RESET 544 //32 REPEAT - Makes a slave an RESET state. | Configuration | 32 | YAAA AAA1 0010 0000 | REPEAT | NO | RESET |  | Makes a slave an RESET state.
STORE_ACTUAL_LEVEL_IN_THE_DTR0 | 545 | #define DALI_STORE_ACTUAL_LEVEL_IN_THE_DTR0 545 //33 REPEAT - Saves the current lighting control level to the DTR (DTR0). (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 33 | YAAA AAA1 0010 0001 | REPEAT | NO | STORE ACTUAL LEVEL IN THE DTR (STORE ACTUAL LEVEL IN DTR0) |  | Saves the current lighting control level to the DTR (DTR0). (In the parenthesis is a name in IEC62386-102ed2.0)
SAVE_PERSISTENT_VARIABLES | 546 | #define DALI_SAVE_PERSISTENT_VARIABLES 546 //34 REPEAT DALI-2 - Saves a variable in nonvolatile memory (NVM). (Command that exist only in IEC62386-102ed2.0) | Configuration | 34 | YAAA AAA1 0010 0010 | REPEAT | NO | SAVE PERSISTENT VARIABLES | DALI-2 | Saves a variable in nonvolatile memory (NVM). (Command that exist only in IEC62386-102ed2.0)
SET_OPERATING_MODE | 547 | #define DALI_SET_OPERATING_MODE 547 //35 REPEAT DALI-2 - Sets data of DTR0 as an operating mode. (Command that exist only in IEC62386-102ed2.0) | Configuration | 35 | YAAA AAA1 0010 0011 | REPEAT | NO | SET OPERATING MODE | DALI-2 | Sets data of DTR0 as an operating mode. (Command that exist only in IEC62386-102ed2.0)
RESET_MEMORY_BANK | 548 | #define DALI_RESET_MEMORY_BANK 548 //36 REPEAT DALI-2 - Changes to the reset value the specified memory bank in DTR0. (Command that exist only in IEC62386-102ed2.0) | Configuration | 36 | YAAA AAA1 0010 0100 | REPEAT | NO | RESET MEMORY BANK | DALI-2 | Changes to the reset value the specified memory bank in DTR0. (Command that exist only in IEC62386-102ed2.0)
IDENTIFY_DEVICE | 549 | #define DALI_IDENTIFY_DEVICE 549 //37 REPEAT DALI-2 - Starts the identification state of the device. (Command that exist only in IEC62386-102ed2.0) | Configuration | 37 | YAAA AAA1 0010 0101 | REPEAT | NO | IDENTIFY DEVICE | DALI-2 | Starts the identification state of the device. (Command that exist only in IEC62386-102ed2.0)
RESERVED38 | 550 | #define DALI_RESERVED38 550 //38 REPEAT - [Reserved] | Configuration | 38 | YAAA AAA1 0010 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED39 | 551 | #define DALI_RESERVED39 551 //39 REPEAT - [Reserved] | Configuration | 39 | YAAA AAA1 0010 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED40 | 552 | #define DALI_RESERVED40 552 //40 REPEAT - [Reserved] | Configuration | 40 | YAAA AAA1 0010 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED41 | 553 | #define DALI_RESERVED41 553 //41 REPEAT - [Reserved] | Configuration | 41 | YAAA AAA1 0010 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
SET_MAX_LEVEL | 554 | #define DALI_SET_MAX_LEVEL 554 //42 REPEAT - Specifies the DTR data as the maximum lighting control level. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 42 | YAAA AAA1 0010 1010 | REPEAT | NO | STORE THE DTR AS MAX LEVEL (SET MAX LEVEL) |  | Specifies the DTR data as the maximum lighting control level. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_MIN_LEVEL | 555 | #define DALI_SET_MIN_LEVEL 555 //43 REPEAT - Specifies the DTR data as the minimum lighting control level. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 43 | YAAA AAA1 0010 1011 | REPEAT | NO | STORE THE DTR AS MIN LEVEL (SET MIN LEVEL) |  | Specifies the DTR data as the minimum lighting control level. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SYSTEM_FAILURE_LEVEL | 556 | #define DALI_SET_SYSTEM_FAILURE_LEVEL 556 //44 REPEAT - Specifies the DTR data as the "FAILURELEVEL". (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 44 | YAAA AAA1 0010 1100 | REPEAT | NO | STORE THE DTR AS SYSTEM FAILURE LEVEL (SET SYSTEM FAILURE LEVEL) |  | Specifies the DTR data as the "FAILURELEVEL". (In the parenthesis is a name in IEC62386-102ed2.0)
SET_POWER_ON_LEVEL | 557 | #define DALI_SET_POWER_ON_LEVEL 557 //45 REPEAT - Specifies the DTR data as the "POWER ONLEVEL". (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 45 | YAAA AAA1 0010 1101 | REPEAT | NO | STORE THE DTR AS POWER ON LEVEL (SET POWER ON LEVEL) |  | Specifies the DTR data as the "POWER ONLEVEL". (In the parenthesis is a name in IEC62386-102ed2.0)
SET_FADE_TIME | 558 | #define DALI_SET_FADE_TIME 558 //46 REPEAT - Specifies the DTR data as the Fade time. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 46 | YAAA AAA1 0010 1110 | REPEAT | NO | STORE THE DTR AS FADE TIME (SET FADE TIME) |  | Specifies the DTR data as the Fade time. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_FADE_RATE | 559 | #define DALI_SET_FADE_RATE 559 //47 REPEAT - Specifies the DTR data as the Fade rate. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 47 | YAAA AAA1 0010 1111 | REPEAT | NO | STORE THE DTR AS FADE RATE (SET FADE RATE) |  | Specifies the DTR data as the Fade rate. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_EXTENDED_FADE_TIME | 560 | #define DALI_SET_EXTENDED_FADE_TIME 560 //48 REPEAT DALI-2 - Specifies the DTR data as the Extended Fade Time. (Command that exist only in IEC62386-102ed2.0) | Configuration | 48 | YAAA AAA1 0011 0000 | REPEAT | NO | SET EXTENDED FADE TIME | DALI-2 | Specifies the DTR data as the Extended Fade Time. (Command that exist only in IEC62386-102ed2.0)
RESERVED49 | 561 | #define DALI_RESERVED49 561 //49 REPEAT - [Reserved] | Configuration | 49 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED50 | 562 | #define DALI_RESERVED50 562 //50 REPEAT - [Reserved] | Configuration | 50 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED51 | 563 | #define DALI_RESERVED51 563 //51 REPEAT - [Reserved] | Configuration | 51 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED52 | 564 | #define DALI_RESERVED52 564 //52 REPEAT - [Reserved] | Configuration | 52 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED53 | 565 | #define DALI_RESERVED53 565 //53 REPEAT - [Reserved] | Configuration | 53 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED54 | 566 | #define DALI_RESERVED54 566 //54 REPEAT - [Reserved] | Configuration | 54 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED55 | 567 | #define DALI_RESERVED55 567 //55 REPEAT - [Reserved] | Configuration | 55 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED56 | 568 | #define DALI_RESERVED56 568 //56 REPEAT - [Reserved] | Configuration | 56 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED57 | 569 | #define DALI_RESERVED57 569 //57 REPEAT - [Reserved] | Configuration | 57 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED58 | 570 | #define DALI_RESERVED58 570 //58 REPEAT - [Reserved] | Configuration | 58 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED59 | 571 | #define DALI_RESERVED59 571 //59 REPEAT - [Reserved] | Configuration | 59 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED60 | 572 | #define DALI_RESERVED60 572 //60 REPEAT - [Reserved] | Configuration | 60 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED61 | 573 | #define DALI_RESERVED61 573 //61 REPEAT - [Reserved] | Configuration | 61 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED62 | 574 | #define DALI_RESERVED62 574 //62 REPEAT - [Reserved] | Configuration | 62 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED63 | 575 | #define DALI_RESERVED63 575 //63 REPEAT - [Reserved] | Configuration | 63 | YAAA AAA1 0011 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
SET_SCENE0 | 576 | #define DALI_SET_SCENE0 576 //64 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 64 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE1 | 577 | #define DALI_SET_SCENE1 577 //65 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 65 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE2 | 578 | #define DALI_SET_SCENE2 578 //66 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 66 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE3 | 579 | #define DALI_SET_SCENE3 579 //67 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 67 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE4 | 580 | #define DALI_SET_SCENE4 580 //68 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 68 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE5 | 581 | #define DALI_SET_SCENE5 581 //69 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 69 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE6 | 582 | #define DALI_SET_SCENE6 582 //70 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 70 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE7 | 583 | #define DALI_SET_SCENE7 583 //71 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 71 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE8 | 584 | #define DALI_SET_SCENE8 584 //72 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 72 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE9 | 585 | #define DALI_SET_SCENE9 585 //73 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 73 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE10 | 586 | #define DALI_SET_SCENE10 586 //74 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 74 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE11 | 587 | #define DALI_SET_SCENE11 587 //75 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 75 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE12 | 588 | #define DALI_SET_SCENE12 588 //76 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 76 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE13 | 589 | #define DALI_SET_SCENE13 589 //77 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 77 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE14 | 590 | #define DALI_SET_SCENE14 590 //78 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 78 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
SET_SCENE15 | 591 | #define DALI_SET_SCENE15 591 //79 REPEAT - Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 79 | YAAA AAA1 0100 XXXX | REPEAT | NO | STORE THE DTR AS SCENE (SET SCENE) |  | Specifies the DTR data as Scene XXXX. (In the parenthesis is a name in IEC62386-102ed2.0)
REMOVE_FROM_SCENE0 | 592 | #define DALI_REMOVE_FROM_SCENE0 592 //80 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 80 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE1 | 593 | #define DALI_REMOVE_FROM_SCENE1 593 //81 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 81 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE2 | 594 | #define DALI_REMOVE_FROM_SCENE2 594 //82 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 82 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE3 | 595 | #define DALI_REMOVE_FROM_SCENE3 595 //83 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 83 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE4 | 596 | #define DALI_REMOVE_FROM_SCENE4 596 //84 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 84 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE5 | 597 | #define DALI_REMOVE_FROM_SCENE5 597 //85 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 85 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE6 | 598 | #define DALI_REMOVE_FROM_SCENE6 598 //86 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 86 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE7 | 599 | #define DALI_REMOVE_FROM_SCENE7 599 //87 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 87 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE8 | 600 | #define DALI_REMOVE_FROM_SCENE8 600 //88 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 88 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE9 | 601 | #define DALI_REMOVE_FROM_SCENE9 601 //89 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 89 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE10 | 602 | #define DALI_REMOVE_FROM_SCENE10 602 //90 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 90 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE11 | 603 | #define DALI_REMOVE_FROM_SCENE11 603 //91 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 91 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE12 | 604 | #define DALI_REMOVE_FROM_SCENE12 604 //92 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 92 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE13 | 605 | #define DALI_REMOVE_FROM_SCENE13 605 //93 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 93 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE14 | 606 | #define DALI_REMOVE_FROM_SCENE14 606 //94 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 94 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
REMOVE_FROM_SCENE15 | 607 | #define DALI_REMOVE_FROM_SCENE15 607 //95 REPEAT - Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.) | Configuration | 95 | YAAA AAA1 0101 XXXX | REPEAT | NO | REMOVE FROM SCENE |  | Deletes the Scene XXXX setting. (Specifies 1111 1111 for the scene register.)
ADD_TO_GROUP0 | 608 | #define DALI_ADD_TO_GROUP0 608 //96 REPEAT - Adds the slave to Group XXXX. | Configuration | 96 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP1 | 609 | #define DALI_ADD_TO_GROUP1 609 //97 REPEAT - Adds the slave to Group XXXX. | Configuration | 97 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP2 | 610 | #define DALI_ADD_TO_GROUP2 610 //98 REPEAT - Adds the slave to Group XXXX. | Configuration | 98 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP3 | 611 | #define DALI_ADD_TO_GROUP3 611 //99 REPEAT - Adds the slave to Group XXXX. | Configuration | 99 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP4 | 612 | #define DALI_ADD_TO_GROUP4 612 //100 REPEAT - Adds the slave to Group XXXX. | Configuration | 100 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP5 | 613 | #define DALI_ADD_TO_GROUP5 613 //101 REPEAT - Adds the slave to Group XXXX. | Configuration | 101 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP6 | 614 | #define DALI_ADD_TO_GROUP6 614 //102 REPEAT - Adds the slave to Group XXXX. | Configuration | 102 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP7 | 615 | #define DALI_ADD_TO_GROUP7 615 //103 REPEAT - Adds the slave to Group XXXX. | Configuration | 103 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP8 | 616 | #define DALI_ADD_TO_GROUP8 616 //104 REPEAT - Adds the slave to Group XXXX. | Configuration | 104 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP9 | 617 | #define DALI_ADD_TO_GROUP9 617 //105 REPEAT - Adds the slave to Group XXXX. | Configuration | 105 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP10 | 618 | #define DALI_ADD_TO_GROUP10 618 //106 REPEAT - Adds the slave to Group XXXX. | Configuration | 106 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP11 | 619 | #define DALI_ADD_TO_GROUP11 619 //107 REPEAT - Adds the slave to Group XXXX. | Configuration | 107 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP12 | 620 | #define DALI_ADD_TO_GROUP12 620 //108 REPEAT - Adds the slave to Group XXXX. | Configuration | 108 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP13 | 621 | #define DALI_ADD_TO_GROUP13 621 //109 REPEAT - Adds the slave to Group XXXX. | Configuration | 109 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP14 | 622 | #define DALI_ADD_TO_GROUP14 622 //110 REPEAT - Adds the slave to Group XXXX. | Configuration | 110 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
ADD_TO_GROUP15 | 623 | #define DALI_ADD_TO_GROUP15 623 //111 REPEAT - Adds the slave to Group XXXX. | Configuration | 111 | YAAA AAA1 0110 XXXX | REPEAT | NO | ADD TO GROUP |  | Adds the slave to Group XXXX.
REMOVE_FROM_GROUP0 | 624 | #define DALI_REMOVE_FROM_GROUP0 624 //112 REPEAT - Deletes the slave from Group XXXX. | Configuration | 112 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP1 | 625 | #define DALI_REMOVE_FROM_GROUP1 625 //113 REPEAT - Deletes the slave from Group XXXX. | Configuration | 113 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP2 | 626 | #define DALI_REMOVE_FROM_GROUP2 626 //114 REPEAT - Deletes the slave from Group XXXX. | Configuration | 114 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP3 | 627 | #define DALI_REMOVE_FROM_GROUP3 627 //115 REPEAT - Deletes the slave from Group XXXX. | Configuration | 115 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP4 | 628 | #define DALI_REMOVE_FROM_GROUP4 628 //116 REPEAT - Deletes the slave from Group XXXX. | Configuration | 116 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP5 | 629 | #define DALI_REMOVE_FROM_GROUP5 629 //117 REPEAT - Deletes the slave from Group XXXX. | Configuration | 117 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP6 | 630 | #define DALI_REMOVE_FROM_GROUP6 630 //118 REPEAT - Deletes the slave from Group XXXX. | Configuration | 118 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP7 | 631 | #define DALI_REMOVE_FROM_GROUP7 631 //119 REPEAT - Deletes the slave from Group XXXX. | Configuration | 119 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP8 | 632 | #define DALI_REMOVE_FROM_GROUP8 632 //120 REPEAT - Deletes the slave from Group XXXX. | Configuration | 120 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP9 | 633 | #define DALI_REMOVE_FROM_GROUP9 633 //121 REPEAT - Deletes the slave from Group XXXX. | Configuration | 121 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP10 | 634 | #define DALI_REMOVE_FROM_GROUP10 634 //122 REPEAT - Deletes the slave from Group XXXX. | Configuration | 122 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP11 | 635 | #define DALI_REMOVE_FROM_GROUP11 635 //123 REPEAT - Deletes the slave from Group XXXX. | Configuration | 123 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP12 | 636 | #define DALI_REMOVE_FROM_GROUP12 636 //124 REPEAT - Deletes the slave from Group XXXX. | Configuration | 124 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP13 | 637 | #define DALI_REMOVE_FROM_GROUP13 637 //125 REPEAT - Deletes the slave from Group XXXX. | Configuration | 125 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP14 | 638 | #define DALI_REMOVE_FROM_GROUP14 638 //126 REPEAT - Deletes the slave from Group XXXX. | Configuration | 126 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
REMOVE_FROM_GROUP15 | 639 | #define DALI_REMOVE_FROM_GROUP15 639 //127 REPEAT - Deletes the slave from Group XXXX. | Configuration | 127 | YAAA AAA1 0111 XXXX | REPEAT | NO | REMOVE FROM GROUP |  | Deletes the slave from Group XXXX.
SET_SHORT_ADDRESS | 640 | #define DALI_SET_SHORT_ADDRESS 640 //128 REPEAT - Specifies the DTR data as a Short Address. (In the parenthesis is a name in IEC62386-102ed2.0) | Configuration | 128 | YAAA AAA1 1000 0000 | REPEAT | NO | STORE DTR AS SHORT ADDRESS (SET SHORT ADDRESS) |  | Specifies the DTR data as a Short Address. (In the parenthesis is a name in IEC62386-102ed2.0)
ENABLE_WRITE_MEMORY | 641 | #define DALI_ENABLE_WRITE_MEMORY 641 //129 REPEAT - Allows writing of the memory bank. | Configuration | 129 | YAAA AAA1 1000 0001 | REPEAT | NO | ENABLE WRITE MEMORY |  | Allows writing of the memory bank.
RESERVED130 | 642 | #define DALI_RESERVED130 642 //130 REPEAT - [Reserved] | Configuration | 130 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED131 | 643 | #define DALI_RESERVED131 643 //131 REPEAT - [Reserved] | Configuration | 131 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED132 | 644 | #define DALI_RESERVED132 644 //132 REPEAT - [Reserved] | Configuration | 132 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED133 | 645 | #define DALI_RESERVED133 645 //133 REPEAT - [Reserved] | Configuration | 133 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED134 | 646 | #define DALI_RESERVED134 646 //134 REPEAT - [Reserved] | Configuration | 134 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED135 | 647 | #define DALI_RESERVED135 647 //135 REPEAT - [Reserved] | Configuration | 135 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED136 | 648 | #define DALI_RESERVED136 648 //136 REPEAT - [Reserved] | Configuration | 136 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED137 | 649 | #define DALI_RESERVED137 649 //137 REPEAT - [Reserved] | Configuration | 137 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED138 | 650 | #define DALI_RESERVED138 650 //138 REPEAT - [Reserved] | Configuration | 138 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED139 | 651 | #define DALI_RESERVED139 651 //139 REPEAT - [Reserved] | Configuration | 139 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED140 | 652 | #define DALI_RESERVED140 652 //140 REPEAT - [Reserved] | Configuration | 140 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED141 | 653 | #define DALI_RESERVED141 653 //141 REPEAT - [Reserved] | Configuration | 141 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED142 | 654 | #define DALI_RESERVED142 654 //142 REPEAT - [Reserved] | Configuration | 142 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
RESERVED143 | 655 | #define DALI_RESERVED143 655 //143 REPEAT - [Reserved] | Configuration | 143 | YAAA AAA1 1000 XXXX | REPEAT | NO | RESERVED |  | [Reserved]
QUERY_STATUS | 144 | #define DALI_QUERY_STATUS 144 //144 - Returns "STATUS INFORMATION" | Query | 144 | YAAA AAA1 1001 0000 |  | STATUS INFORMATION | QUERY STATUS |  | Returns "STATUS INFORMATION" | ‘STATUS INFORMATION’ : 8-bit data indicating the status of a ballast. The meanings of the bits are as follows: bit0 Status of control gear<0>=OK bit1 Lamp failure(cmd146) <0>=OK bit2 Lamp arc power on(cmd147) <0>=OFF bit3 Query Limit Error(cmd148) <0>=YES bit4 Fade running<0>=fade is ready <1>=fade is running bit5 Query RESET STATE(cmd149) <0>=No bit6 Query Missing short address(cmd150) <0>=No bit7 Query POWER FAILURE(cmd155) <0>=No
QUERY_CONTROL_GEAR_PRESENT | 145 | #define DALI_QUERY_CONTROL_GEAR_PRESENT 145 //145 - Is there a slave that can communicate? (In the parenthesis is a name in IEC62386-102ed2.0) | Query | 145 | YAAA AAA1 1001 0001 |  | YES/NO | QUERY CONTROL GEAR (QUERY CONTROL GEAR PRESENT) |  | Is there a slave that can communicate? (In the parenthesis is a name in IEC62386-102ed2.0)
QUERY_LAMP_FAILURE | 146 | #define DALI_QUERY_LAMP_FAILURE 146 //146 - Is there a lamp problem? | Query | 146 | YAAA AAA1 1001 0010 |  | YES/NO | QUERY LAMP FAILURE |  | Is there a lamp problem? | ‘LAMP FAILURE’ : The Lamp Failure status of IEC62386-207 time is set on the following conditions. The following bit (0-4) of FAILURE STATUS will be determined to LampFailure in the case that has been set even 1. bit0 short circuit bit1 open circuit bit2 load decrease bit3 load increase bit4 current protector active
QUERY_LAMP_POWER_ON | 147 | #define DALI_QUERY_LAMP_POWER_ON 147 //147 - Is a lamp on? | Query | 147 | YAAA AAA1 1001 0011 |  | YES/NO | QUERY LAMP POWER ON |  | Is a lamp on?
QUERY_LIMIT_ERROR | 148 | #define DALI_QUERY_LIMIT_ERROR 148 //148 - Is the specified lighting control level out of the range from the minimum to the maximum values? | Query | 148 | YAAA AAA1 1001 0100 |  | YES/NO | QUERY LIMIT ERROR |  | Is the specified lighting control level out of the range from the minimum to the maximum values?
QUERY_RESET_STATE | 149 | #define DALI_QUERY_RESET_STATE 149 //149 - Is the slave in 'RESET STATE'? | Query | 149 | YAAA AAA1 1001 0101 |  | YES/NO | QUERY RESET STATE |  | Is the slave in 'RESET STATE'?
QUERY_MISSING_SHORT_ADDRESS | 150 | #define DALI_QUERY_MISSING_SHORT_ADDRESS 150 //150 - Does the slave not have a short address? | Query | 150 | YAAA AAA1 1001 0110 |  | YES/NO | QUERY MISSING SHORT ADDRESS |  | Does the slave not have a short address?
QUERY_VERSION_NUMBER | 151 | #define DALI_QUERY_VERSION_NUMBER 151 //151 - What is the corresponding IEC standard number? | Query | 151 | YAAA AAA1 1001 0111 |  | Standard number | QUERY VERSION NUMBER |  | What is the corresponding IEC standard number?
QUERY_CONTENT_DTR0 | 152 | #define DALI_QUERY_CONTENT_DTR0 152 //152 - What is the DTR content? (In the parenthesis is a name in IEC62386-102ed2.0) | Query | 152 | YAAA AAA1 1001 1000 |  | DTR content | QUERY CONTENT DTR (QUERY CONTENT DTR0) |  | What is the DTR content? (In the parenthesis is a name in IEC62386-102ed2.0)
QUERY_DEVICE_TYPE | 153 | #define DALI_QUERY_DEVICE_TYPE 153 //153 - What is the device type? (fluorescent lamp:0000 0000) (IEC62386-207 is 6 fixed) | Query | 153 | YAAA AAA1 1001 1001 |  | Device type | QUERY DEVICE TYPE |  | What is the device type? (fluorescent lamp:0000 0000) (IEC62386-207 is 6 fixed) | ‘DEVICE TYPE’ : Part number,Device Type,Description 201,0,Fluorescent lamps (device type 0) 202,1,Built-in emergency lighting (device type 1) 203,2,Discharge lamps (excluding fluorescent lamps) (device type 2) 204,3,Low-voltage halogen lamps (device type 3) 205,4,The power supply voltage controller for incandescent lamps (device type 4) 206,5,Conversion to the DC voltage of the digital signal (device type 5) 207,6,LED model (device type 6) 208,7,Switching feature (device type 7) 209,8,Color control (device type 8) 210,9,Sequencer (device type 9) If Part2xx has not been incorporated into the system, and responds as follows. -IEC62386-102ed1.0 It is not assumed there is no extended standard on the standard. It is a specification to return 6 by default in Applilet EZ for HCD. When not selecting 207 modes, it is not supported 207. -IEC62386-102ed2.0254：Part2xx is not implemented
QUERY_PHYSICAL_MINIMUM_LEVEL | 154 | #define DALI_QUERY_PHYSICAL_MINIMUM_LEVEL 154 //154 - What is the minimum lighting control level specified by the hardware? | Query | 154 | YAAA AAA1 1001 1010 |  | Minimum limit on the hardware | QUERY PHYSICAL MINIMUM LEVEL |  | What is the minimum lighting control level specified by the hardware?
QUERY_POWER_FAILURE | 155 | #define DALI_QUERY_POWER_FAILURE 155 //155 - Has the slave operated without the execution of reset-command or the adjustment of the lighting control level? | Query | 155 | YAAA AAA1 1001 1011 |  | YES/NO | QUERY POWER FAILURE |  | Has the slave operated without the execution of reset-command or the adjustment of the lighting control level?
QUERY_CONTENT_DTR1 | 156 | #define DALI_QUERY_CONTENT_DTR1 156 //156 - What is the DTR1 content? | Query | 156 | YAAA AAA1 1001 1100 |  | DTR1 content | QUERY CONTENT DTR1 |  | What is the DTR1 content?
QUERY_CONTENT_DTR2 | 157 | #define DALI_QUERY_CONTENT_DTR2 157 //157 - What is the DTR2 content? | Query | 157 | YAAA AAA1 1001 1101 |  | DTR2 content | QUERY CONTENT DTR2 |  | What is the DTR2 content?
QUERY_OPERATING_MODE | 158 | #define DALI_QUERY_OPERATING_MODE 158 //158 DALI-2 - What is the Operating Mode? (Only IEC62386-102ed2.0 ) | Query | 158 | YAAA AAA1 1001 1110 |  | OperatingMode | QUERY OPERATING MODE | DALI-2 | What is the Operating Mode? (Only IEC62386-102ed2.0 )
QUERY_LIGHT_SOURCE_TYPE | 159 | #define DALI_QUERY_LIGHT_SOURCE_TYPE 159 //159 DALI-2 - What is the Light source type? (Only IEC62386-102ed2.0 ) | Query | 159 | YAAA AAA1 1001 1111 |  | Light source type | QUERY LIGHT SOURCE TYPE | DALI-2 | What is the Light source type? (Only IEC62386-102ed2.0 )
QUERY_ACTUAL_LEVEL | 160 | #define DALI_QUERY_ACTUAL_LEVEL 160 //160 - What is the "ACTUAL LEVEL" (the current lighting control level)? | Query | 160 | YAAA AAA1 1010 0000 |  | ACTUAL LEVEL | QUERY ACTUAL LEVEL |  | What is the "ACTUAL LEVEL" (the current lighting control level)?
QUERY_MAX_LEVEL | 161 | #define DALI_QUERY_MAX_LEVEL 161 //161 - What is the maximum lighting control level? | Query | 161 | YAAA AAA1 1010 0001 |  | Maximum lighting control level | QUERY MAX LEVEL |  | What is the maximum lighting control level?
QUERY_MIN_LEVEL | 162 | #define DALI_QUERY_MIN_LEVEL 162 //162 - What is the minimum lighting control level? | Query | 162 | YAAA AAA1 1010 0010 |  | Minimum lighting control level | QUERY MIN LEVEL |  | What is the minimum lighting control level?
QUERY_POWER_ON_LEVEL | 163 | #define DALI_QUERY_POWER_ON_LEVEL 163 //163 - What is the "POWER ON LEVEL" (the lighting control level when the power is turned on)? | Query | 163 | YAAA AAA1 1010 0011 |  | POWER ON LEVEL | QUERY POWER ON LEVEL |  | What is the "POWER ON LEVEL" (the lighting control level when the power is turned on)?
QUERY_SYSTEM_FAILURE_LEVEL | 164 | #define DALI_QUERY_SYSTEM_FAILURE_LEVEL 164 //164 - What is the "SYSTEM FAILURE LEVEL" (the lighting control level when a failure occurs)? | Query | 164 | YAAA AAA1 1010 0100 |  | FAILURE LEVEL | QUERY SYSTEM FAILURE LEVEL |  | What is the "SYSTEM FAILURE LEVEL" (the lighting control level when a failure occurs)?
QUERY_FADE_TIME_FADE_RATE | 165 | #define DALI_QUERY_FADE_TIME_FADE_RATE 165 //165 - What are the Fade time and Fade rate? | Query | 165 | YAAA AAA1 1010 0101 |  | <Higher> Time <Lower> Rate | QUERY FADE TIME/FADE RATE |  | What are the Fade time and Fade rate?
QUERY_MANUFACTURER_SPECIFIC_MODE | 166 | #define DALI_QUERY_MANUFACTURER_SPECIFIC_MODE 166 //166 DALI-2 - What is the Specific Mode? (Command that exist only in IEC62386-102ed2.0) | Query | 166 | YAAA AAA1 1010 0110 |  | SpecificMode | QUERY MANUFACTURER SPECIFIC MODE | DALI-2 | What is the Specific Mode? (Command that exist only in IEC62386-102ed2.0)
QUERY_NEXT_DEVICE_TYPE | 167 | #define DALI_QUERY_NEXT_DEVICE_TYPE 167 //167 DALI-2 - What is the next Device Type? (Command that exist only in IEC62386-102ed2.0) | Query | 167 | YAAA AAA1 1010 0111 |  | Next DeviceType | QUERY NEXT DEVICE TYPE | DALI-2 | What is the next Device Type? (Command that exist only in IEC62386-102ed2.0)
QUERY_EXTENDED_FADE_TIME | 168 | #define DALI_QUERY_EXTENDED_FADE_TIME 168 //168 DALI-2 - What is the Extended Fade Time? (Command that exist only in IEC62386-102ed2.0) | Query | 168 | YAAA AAA1 1010 1000 |  | SpecificMode | QUERY EXTENDED FADE TIME | DALI-2 | What is the Extended Fade Time? (Command that exist only in IEC62386-102ed2.0)
QUERY_CONTROL_GEAR_FAILURE | 169 | #define DALI_QUERY_CONTROL_GEAR_FAILURE 169 //169 DALI-2 - Does a slave have the abnormality? (Command that exist only in IEC62386-102ed2.0) | Query | 169 | YAAA AAA1 1010 1010 |  | SpecificMode | QUERY CONTROL GEAR FAILURE | DALI-2 | Does a slave have the abnormality? (Command that exist only in IEC62386-102ed2.0)
RESERVED170 | 170 | #define DALI_RESERVED170 170 //170 - [Reserved] | Query | 170 | YAAA AAA1 1010 XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED171 | 171 | #define DALI_RESERVED171 171 //171 - [Reserved] | Query | 171 | YAAA AAA1 1010 XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED172 | 172 | #define DALI_RESERVED172 172 //172 - [Reserved] | Query | 172 | YAAA AAA1 1010 XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED173 | 173 | #define DALI_RESERVED173 173 //173 - [Reserved] | Query | 173 | YAAA AAA1 1010 XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED174 | 174 | #define DALI_RESERVED174 174 //174 - [Reserved] | Query | 174 | YAAA AAA1 1010 XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED175 | 175 | #define DALI_RESERVED175 175 //175 - [Reserved] | Query | 175 | YAAA AAA1 1010 XXXX |  | NO | RESERVED |  | [Reserved]
QUERY_SCENE0_LEVEL | 176 | #define DALI_QUERY_SCENE0_LEVEL 176 //176 - What is the lighting control level for SCENE XXXX? | Query | 176 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE1_LEVEL | 177 | #define DALI_QUERY_SCENE1_LEVEL 177 //177 - What is the lighting control level for SCENE XXXX? | Query | 177 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE2_LEVEL | 178 | #define DALI_QUERY_SCENE2_LEVEL 178 //178 - What is the lighting control level for SCENE XXXX? | Query | 178 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE3_LEVEL | 179 | #define DALI_QUERY_SCENE3_LEVEL 179 //179 - What is the lighting control level for SCENE XXXX? | Query | 179 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE4_LEVEL | 180 | #define DALI_QUERY_SCENE4_LEVEL 180 //180 - What is the lighting control level for SCENE XXXX? | Query | 180 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE5_LEVEL | 181 | #define DALI_QUERY_SCENE5_LEVEL 181 //181 - What is the lighting control level for SCENE XXXX? | Query | 181 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE6_LEVEL | 182 | #define DALI_QUERY_SCENE6_LEVEL 182 //182 - What is the lighting control level for SCENE XXXX? | Query | 182 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE7_LEVEL | 183 | #define DALI_QUERY_SCENE7_LEVEL 183 //183 - What is the lighting control level for SCENE XXXX? | Query | 183 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE8_LEVEL | 184 | #define DALI_QUERY_SCENE8_LEVEL 184 //184 - What is the lighting control level for SCENE XXXX? | Query | 184 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE9_LEVEL | 185 | #define DALI_QUERY_SCENE9_LEVEL 185 //185 - What is the lighting control level for SCENE XXXX? | Query | 185 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE10_LEVEL | 186 | #define DALI_QUERY_SCENE10_LEVEL 186 //186 - What is the lighting control level for SCENE XXXX? | Query | 186 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE11_LEVEL | 187 | #define DALI_QUERY_SCENE11_LEVEL 187 //187 - What is the lighting control level for SCENE XXXX? | Query | 187 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE12_LEVEL | 188 | #define DALI_QUERY_SCENE12_LEVEL 188 //188 - What is the lighting control level for SCENE XXXX? | Query | 188 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE13_LEVEL | 189 | #define DALI_QUERY_SCENE13_LEVEL 189 //189 - What is the lighting control level for SCENE XXXX? | Query | 189 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE14_LEVEL | 190 | #define DALI_QUERY_SCENE14_LEVEL 190 //190 - What is the lighting control level for SCENE XXXX? | Query | 190 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_SCENE15_LEVEL | 191 | #define DALI_QUERY_SCENE15_LEVEL 191 //191 - What is the lighting control level for SCENE XXXX? | Query | 191 | YAAA AAA1 1011 XXXX |  | Lighting control level | QUERY SCENE LEVEL (SCENES 0-15) |  | What is the lighting control level for SCENE XXXX?
QUERY_GROUPS_0_7 | 192 | #define DALI_QUERY_GROUPS_0_7 192 //192 - Does the slave belong to a group among groups 0 to 7? (Each bit corresponds to agroup.) | Query | 192 | YAAA AAA1 1100 0000 |  | <0>No or <1>Yes for each bit | QUERY GROUPS 0-7 |  | Does the slave belong to a group among groups 0 to 7? (Each bit corresponds to agroup.)
QUERY_GROUPS_8_15 | 193 | #define DALI_QUERY_GROUPS_8_15 193 //193 - Does the slave belong to a group among groups 8 to 15? (Each bit corresponds to agroup.) | Query | 193 | YAAA AAA1 1100 0001 |  | <0>No or <1>Yes for each bit | QUERY GROUPS 8-15 |  | Does the slave belong to a group among groups 8 to 15? (Each bit corresponds to agroup.)
QUERY_RANDOM_ADDRESS_H | 194 | #define DALI_QUERY_RANDOM_ADDRESS_H 194 //194 - What are the higher 8 bits of the random address? | Query | 194 | YAAA AAA1 1100 0010 |  | Random address (high) | QUERY RANDOM ADDRESS (H) |  | What are the higher 8 bits of the random address?
QUERY_RANDOM_ADDRESS_M | 195 | #define DALI_QUERY_RANDOM_ADDRESS_M 195 //195 - What are the middle 8 bits of the random address? | Query | 195 | YAAA AAA1 1100 0011 |  | Random address (middle) | QUERY RANDOM ADDRESS (M) |  | What are the middle 8 bits of the random address?
QUERY_RANDOM_ADDRESS_L | 196 | #define DALI_QUERY_RANDOM_ADDRESS_L 196 //196 - What are the lower 8 bits of the random address? | Query | 196 | YAAA AAA1 1100 0100 |  | Random address (low) | QUERY RANDOM ADDRESS (L) |  | What are the lower 8 bits of the random address?
READ_MEMORY_LOCATION | 197 | #define DALI_READ_MEMORY_LOCATION 197 //197 - What is the memory location content? | Query | 197 | YAAA AAA1 1100 0101 |  | Memory location content | READ MEMORY LOCATION |  | What is the memory location content?
RESERVED198 | 198 | #define DALI_RESERVED198 198 //198 - [Reserved] | Query | 198 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED199 | 199 | #define DALI_RESERVED199 199 //199 - [Reserved] | Query | 199 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED200 | 200 | #define DALI_RESERVED200 200 //200 - [Reserved] | Query | 200 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED201 | 201 | #define DALI_RESERVED201 201 //201 - [Reserved] | Query | 201 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED202 | 202 | #define DALI_RESERVED202 202 //202 - [Reserved] | Query | 202 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED203 | 203 | #define DALI_RESERVED203 203 //203 - [Reserved] | Query | 203 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED204 | 204 | #define DALI_RESERVED204 204 //204 - [Reserved] | Query | 204 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED205 | 205 | #define DALI_RESERVED205 205 //205 - [Reserved] | Query | 205 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED206 | 206 | #define DALI_RESERVED206 206 //206 - [Reserved] | Query | 206 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED207 | 207 | #define DALI_RESERVED207 207 //207 - [Reserved] | Query | 207 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED208 | 208 | #define DALI_RESERVED208 208 //208 - [Reserved] | Query | 208 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED209 | 209 | #define DALI_RESERVED209 209 //209 - [Reserved] | Query | 209 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED210 | 210 | #define DALI_RESERVED210 210 //210 - [Reserved] | Query | 210 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED211 | 211 | #define DALI_RESERVED211 211 //211 - [Reserved] | Query | 211 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED212 | 212 | #define DALI_RESERVED212 212 //212 - [Reserved] | Query | 212 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED213 | 213 | #define DALI_RESERVED213 213 //213 - [Reserved] | Query | 213 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED214 | 214 | #define DALI_RESERVED214 214 //214 - [Reserved] | Query | 214 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED215 | 215 | #define DALI_RESERVED215 215 //215 - [Reserved] | Query | 215 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED216 | 216 | #define DALI_RESERVED216 216 //216 - [Reserved] | Query | 216 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED217 | 217 | #define DALI_RESERVED217 217 //217 - [Reserved] | Query | 217 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED218 | 218 | #define DALI_RESERVED218 218 //218 - [Reserved] | Query | 218 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED219 | 219 | #define DALI_RESERVED219 219 //219 - [Reserved] | Query | 219 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED220 | 220 | #define DALI_RESERVED220 220 //220 - [Reserved] | Query | 220 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED221 | 221 | #define DALI_RESERVED221 221 //221 - [Reserved] | Query | 221 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED222 | 222 | #define DALI_RESERVED222 222 //222 - [Reserved] | Query | 222 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED223 | 223 | #define DALI_RESERVED223 223 //223 - [Reserved] | Query | 223 | YAAA AAA1 110X XXXX |  | NO | RESERVED |  | [Reserved]
REFERENCE_SYSTEM_POWER | 224 | #define DALI_REFERENCE_SYSTEM_POWER 224 //224 IEC62386-207 - Starts power measurement. (Command that exist only in IEC62386-207) | Application extended configuration | 224 | YAAA AAA1 11100000 |  | NO | REFERENCE SYSTEM POWER | IEC62386-207 | Starts power measurement. (Command that exist only in IEC62386-207)
ENABLE_CURRENT_PROTECTOR | 225 | #define DALI_ENABLE_CURRENT_PROTECTOR 225 //225 IEC62386-207 - Enables the current protection. (Command that exist only in IEC62386-207) | Application extended configuration | 225 | YAAA AAA1 11100001 |  | NO | ENABLE CURRENT PROTECTOR | IEC62386-207 | Enables the current protection. (Command that exist only in IEC62386-207)
DISABLE_CURRENT_PROTECTOR | 226 | #define DALI_DISABLE_CURRENT_PROTECTOR 226 //226 IEC62386-207 - Disables the current protection. (Command that exist only in IEC62386-207) | Application extended configuration | 226 | YAAA AAA1 11100010 |  | NO | DISABLE CURRENT PROTECTOR | IEC62386-207 | Disables the current protection. (Command that exist only in IEC62386-207)
SELECT_DIMMING_CURVE | 227 | #define DALI_SELECT_DIMMING_CURVE 227 //227 IEC62386-207 - Selects Dimming curve. (Command that exist only in IEC62386-207) | Application extended configuration | 227 | YAAA AAA1 11100011 |  | NO | SELECT DIMMING CURVE | IEC62386-207 | Selects Dimming curve. (Command that exist only in IEC62386-207)
STORE_DTR_AS_FAST_FADE_TIME | 228 | #define DALI_STORE_DTR_AS_FAST_FADE_TIME 228 //228 IEC62386-207 - Sets the DTR of the data as Fast Fade Time.(Command that exist only in IEC62386-207) | Application extended configuration | 228 | YAAA AAA1 11100100 |  | NO | STORE DTR AS FAST FADE TIME | IEC62386-207 | Sets the DTR of the data as Fast Fade Time.(Command that exist only in IEC62386-207)
RESERVED229 | 229 | #define DALI_RESERVED229 229 //229 - [Reserved] | Application extended configuration | 229 | YAAA AAA1 1110 XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED230 | 230 | #define DALI_RESERVED230 230 //230 - [Reserved] | Application extended configuration | 230 | YAAA AAA1 1110 XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED231 | 231 | #define DALI_RESERVED231 231 //231 - [Reserved] | Application extended configuration | 231 | YAAA AAA1 1110 XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED232 | 232 | #define DALI_RESERVED232 232 //232 - [Reserved] | Application extended configuration | 232 | YAAA AAA1 1110 XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED233 | 233 | #define DALI_RESERVED233 233 //233 - [Reserved] | Application extended configuration | 233 | YAAA AAA1 1110 XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED234 | 234 | #define DALI_RESERVED234 234 //234 - [Reserved] | Application extended configuration | 234 | YAAA AAA1 1110 XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED235 | 235 | #define DALI_RESERVED235 235 //235 - [Reserved] | Application extended configuration | 235 | YAAA AAA1 1110 XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED236 | 236 | #define DALI_RESERVED236 236 //236 - [Reserved] | Application extended configuration | 236 | YAAA AAA1 1110 XXXX |  | NO | RESERVED |  | [Reserved]
QUERY_GEAR_TYPE | 237 | #define DALI_QUERY_GEAR_TYPE 237 //237 IEC62386-207 - Returns ‘GEAR TYPE’ (Command that exist only in IEC62386-207) | Application extended query | 237 | YAAA AAA1 11101101 |  | GEAR TYPE | QUERY GEAR TYPE | IEC62386-207 | Returns ‘GEAR TYPE’ (Command that exist only in IEC62386-207) | 8-bit data indicating GEAR TYPE. The meanings of the bits are as follows: bit0 LED power supply integrated bit1 LED module integrated bit2 a.c. supply possible bit3 d.c. supply possible bit4-7 unused
QUERY_DIMMING_CURVE | 238 | #define DALI_QUERY_DIMMING_CURVE 238 //238 IEC62386-207 - Returns ’Dimming curve’in use (Command that exist only in IEC62386-207) | Application extended query | 238 | YAAA AAA1 11101110 |  | Dimming curve number | QUERY DIMMING CURVE | IEC62386-207 | Returns ’Dimming curve’in use (Command that exist only in IEC62386-207)
QUERY_POSSIBLE_OPERATING_MODE | 239 | #define DALI_QUERY_POSSIBLE_OPERATING_MODE 239 //239 IEC62386-207 - Returns ‘POSSIBLEG OPERATING MODE’ (Command that exist only in IEC62386-207) | Application extended query | 239 | YAAA AAA1 11101111 |  | POSSIBLE OPERATION MODE | QUERY POSSIBLE OPERATING MODE | IEC62386-207 | Returns ‘POSSIBLEG OPERATING MODE’ (Command that exist only in IEC62386-207) | 8-bit data indicating POSSIBLE OPERATING MODE. The meanings of the bits are as follows: bit0 PWM mode is possible bit1 AM mode is possible bit2 output is current controlled bit3 high current pulse bit4-7 unused
QUERY_FEATURES | 240 | #define DALI_QUERY_FEATURES 240 //240 IEC62386-207 - Returns ‘FEATURES’ (Command that exist only in IEC62386-207) | Application extended query | 240 | YAAA AAA1 11110000 |  | FEATURE | QUERY FEATURES | IEC62386-207 | Returns ‘FEATURES’ (Command that exist only in IEC62386-207) | 8-bit data indicating FEATURES. The meanings of the bits are as follows: bit0 short circuit detection can be queried bit1 open circuit detection can be queried bit2 detection of load decrease can be queried bit3 detection of load increase can be queried bit4 current protestor is implemented and can be queried bit5 thermal shut down can be queried bit6 light level reduction due to over temperature can be queried bit7 physical selection supported
QUERY_FAILURE_STATUS | 241 | #define DALI_QUERY_FAILURE_STATUS 241 //241 IEC62386-207 - Returns ‘FAILURE STATUS’ (Command that exist only in IEC62386-207) | Application extended query | 241 | YAAA AAA1 11110001 |  | FAILURE STATUS | QUERY FAILURE STATUS | IEC62386-207 | Returns ‘FAILURE STATUS’ (Command that exist only in IEC62386-207) | 8-bit data indicating FEATURES. The meanings of the bits are as follows: bit0 short circuit bit1 open circuit bit2 load decrease bit3 load increase bit4 current protestor active bit5 thermal shut down
QUERY_SHORT_CIRCUIT | 242 | #define DALI_QUERY_SHORT_CIRCUIT 242 //242 IEC62386-207 - Returns bit0 short circuit of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207) | Application extended query | 242 | YAAA AAA1 11110010 |  | YES/NO | QUERY SHORT CIRCUIT | IEC62386-207 | Returns bit0 short circuit of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207)
QUERY_OPEN_CIRCUIT | 243 | #define DALI_QUERY_OPEN_CIRCUIT 243 //243 IEC62386-207 - Returns bit1 open circuit of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207) | Application extended query | 243 | YAAA AAA1 11110011 |  | YES/NO | QUERY OPEN CIRCUIT | IEC62386-207 | Returns bit1 open circuit of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207)
QUERY_LOAD_DECREASE | 244 | #define DALI_QUERY_LOAD_DECREASE 244 //244 IEC62386-207 - Returns bit2 load decrease of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207) | Application extended query | 244 | YAAA AAA1 11110100 |  | YES/NO | QUERY LOAD DECREASE | IEC62386-207 | Returns bit2 load decrease of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207)
QUERY_LOAD_INDREASE | 245 | #define DALI_QUERY_LOAD_INDREASE 245 //245 IEC62386-207 - Returns bit3 load increase of‘FAILURE STATUS’ (Command that exist only in IEC62386-207) | Application extended query | 245 | YAAA AAA1 11110101 |  | YES/NO | QUERY LOAD INDREASE | IEC62386-207 | Returns bit3 load increase of‘FAILURE STATUS’ (Command that exist only in IEC62386-207)
QUERY_CURRENT_PROTECTOR_ACTIVE | 246 | #define DALI_QUERY_CURRENT_PROTECTOR_ACTIVE 246 //246 IEC62386-207 - Returns bit4 current protector active of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207) | Application extended query | 246 | YAAA AAA1 11110110 |  | YES/NO | QUERY CURRENT PROTECTOR ACTIVE | IEC62386-207 | Returns bit4 current protector active of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207)
QUERY_THERMAL_SHUTDOWN | 247 | #define DALI_QUERY_THERMAL_SHUTDOWN 247 //247 IEC62386-207 - Returns bit5 thermal shut down of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207) | Application extended query | 247 | YAAA AAA1 11110111 |  | YES/NO | QUERY THERMAL SHUTDOWN | IEC62386-207 | Returns bit5 thermal shut down of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207)
QUERY_THERMAL_OVERLOAD | 248 | #define DALI_QUERY_THERMAL_OVERLOAD 248 //248 IEC62386-207 - Returns bit6 thermal overload with light level reduction of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207) | Application extended query | 248 | YAAA AAA1 11111000 |  | YES/NO | QUERY THERMAL OVERLOAD | IEC62386-207 | Returns bit6 thermal overload with light level reduction of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207)
QUERY_REFARENCE_RUNNING | 249 | #define DALI_QUERY_REFARENCE_RUNNING 249 //249 IEC62386-207 - Returns whetherReference System Power is in operation. (Command that exist only in IEC62386-207) | Application extended query | 249 | YAAA AAA1 11111001 |  | YES/NO | QUERY REFARENCE RUNNING | IEC62386-207 | Returns whetherReference System Power is in operation. (Command that exist only in IEC62386-207)
QUERY_REFERENCE_MEASURMENT_FAILED | 250 | #define DALI_QUERY_REFERENCE_MEASURMENT_FAILED 250 //250 IEC62386-207 - Returns bit7 reference measurement failed of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207) | Application extended query | 250 | YAAA AAA1 11111010 |  | YES/NO | QUERY REFERENCE MEASURMENT FAILED | IEC62386-207 | Returns bit7 reference measurement failed of ‘FAILURE STATUS’ (Command that exist only in IEC62386-207)
QUERY_CURRENT_PROTECTOR_ENABLE | 251 | #define DALI_QUERY_CURRENT_PROTECTOR_ENABLE 251 //251 IEC62386-207 - Returns state of Curent protector (Command that exist only in IEC62386-207) | Application extended query | 251 | YAAA AAA1 11111011 |  | YES/NO | QUERY CURRENT PROTECTOR ENABLE | IEC62386-207 | Returns state of Curent protector (Command that exist only in IEC62386-207)
QUERY_OPERATING_MODE | 252 | #define DALI_QUERY_OPERATING_MODE 252 //252 IEC62386-207 - Returns ‘OPERATING MODE’ (Command that exist only in IEC62386-207) | Application extended query | 252 | YAAA AAA1 11111100 |  | OPERATION MODE | QUERY OPERATING MODE | IEC62386-207 | Returns ‘OPERATING MODE’ (Command that exist only in IEC62386-207) | 8-bit data indicating OPARATING MODE. The meanings of the bits are as follows: bit0 PWM mode active bit1 AM mode active bit2 output is current controlled bit3 high current pulse mode is active bit4 non-logarithmic dimming curve active bit5-7 unused
QUERY_FAST_FADE_TIME | 253 | #define DALI_QUERY_FAST_FADE_TIME 253 //253 IEC62386-207 - Returns set Fast fade time. (Command that exist only in IEC62386-207) | Application extended query | 253 | YAAA AAA1 11111101 |  | Fast fade time | QUERY FAST FADE TIME | IEC62386-207 | Returns set Fast fade time. (Command that exist only in IEC62386-207)
QUERY_MIN_FAST_FADE_TIME | 254 | #define DALI_QUERY_MIN_FAST_FADE_TIME 254 //254 IEC62386-207 - Returns set Minimum fast fade time (Command that exist only in IEC62386-207) | Application extended query | 254 | YAAA AAA1 11111110 |  | Minumum fast fade time | QUERY MIN FAST FADE TIME | IEC62386-207 | Returns set Minimum fast fade time (Command that exist only in IEC62386-207)
QUERY_EXTENDED_VERSION_NUMBER | 255 | #define DALI_QUERY_EXTENDED_VERSION_NUMBER 255 //255 IEC62386-207 - The version number of the extended support? IEC62386-207: 1, Other: NO(no response) | Application extended query | 255 | YAAA AAA1 1111 1111 |  | 1 or NO (no response) | QUERY EXTENDED VERSION NUMBER | IEC62386-207 | The version number of the extended support? IEC62386-207: 1, Other: NO(no response)
TERMINATE | 0x01A1 | #define DALI_TERMINATE 0x01A1 //256 - Releases the INITIALISE state. | Special | 256 | 1010 0001 0000 0000 |  | NO | TERMINATE |  | Releases the INITIALISE state.
DATA_TRANSFER_REGISTER0 | 0x01A3 | #define DALI_DATA_TRANSFER_REGISTER0 0x01A3 //257 - Stores the data XXXX XXXX to the DTR(DTR0). (In the parenthesis is a name in IEC62386-102ed2.0) | Special | 257 | 1010 0011 XXXX XXXX |  | NO | DATA TRANSFER REGISTER(DTR) (DTR0) |  | Stores the data XXXX XXXX to the DTR(DTR0). (In the parenthesis is a name in IEC62386-102ed2.0)
INITIALISE | 0x03A5 | #define DALI_INITIALISE 0x03A5 //258 REPEAT - Sets the slave to the INITIALISE status for15 minutes. Commands 259 to 270 are enabled only for a slave in this status. | Special | 258 | 1010 0101 XXXX XXXX | REPEAT | NO | INITIALISE |  | Sets the slave to the INITIALISE status for15 minutes. Commands 259 to 270 are enabled only for a slave in this status. | Target slave specification of INITIALISE (XXXX XXXX) 0000 0000: All slaves is target 0AAA AAA1: Address AAAAAA is target 1111 1111: A slave without Short Address is target
RANDOMISE | 0x03A7 | #define DALI_RANDOMISE 0x03A7 //259 REPEAT - Generates a random address. | Special | 259 | 1010 0111 0000 0000 | REPEAT | NO | RANDOMISE |  | Generates a random address.
COMPARE | 0x01A9 | #define DALI_COMPARE 0x01A9 //260 - Is the random address smaller or equal to the search address? | Special | 260 | 1010 1001 0000 0000 |  | YES/NO | COMPARE |  | Is the random address smaller or equal to the search address?
WITHDRAW | 0x01AB | #define DALI_WITHDRAW 0x01AB //261 - Excludes slaves for which the random address and search address match from the Compare process. | Special | 261 | 1010 1011 0000 0000 |  | NO | WITHDRAW |  | Excludes slaves for which the random address and search address match from the Compare process.
RESERVED262 | 0x01AD | #define DALI_RESERVED262 0x01AD //262 - [Reserved] | Special | 262 | 1010 1101 0000 0000 |  | NO | RESERVED |  | [Reserved]
PING | 0x01AF | #define DALI_PING 0x01AF //263 DALI-2 - Ignores in the slave. (Command that exist only in IEC62386-102ed2.0) | Special | 263 | 1010 1111 0000 0000 |  | NO | PING | DALI-2 | Ignores in the slave. (Command that exist only in IEC62386-102ed2.0)
SEARCHADDRH | 0x01B1 | #define DALI_SEARCHADDRH 0x01B1 //264 - Specifies the higher 8 bits of the search address. | Special | 264 | 1011 0001 HHHH HHHH |  | NO | SEARCHADDRH |  | Specifies the higher 8 bits of the search address.
SEARCHADDRM | 0x01B3 | #define DALI_SEARCHADDRM 0x01B3 //265 - Specifies the middle 8 bits of the search address. | Special | 265 | 1011 0011 MMMM MMMM |  | NO | SEARCHADDRM |  | Specifies the middle 8 bits of the search address.
SEARCHADDRL | 0x01B5 | #define DALI_SEARCHADDRL 0x01B5 //266 - Specifies the lower 8 bits of the search address. | Special | 266 | 1011 0101 LLLL LLLL |  | NO | SEARCHADDRL |  | Specifies the lower 8 bits of the search address.
PROGRAM_SHORT_ADDRESS | 0x01B7 | #define DALI_PROGRAM_SHORT_ADDRESS 0x01B7 //267 - The slave shall store the received 6-bit address (AAA AAA) as a short address if it is selected. | Special | 267 | 1011 0111 0AAA AAA1 |  | NO | PROGRAM SHORT ADDRESS |  | The slave shall store the received 6-bit address (AAA AAA) as a short address if it is selected. | It is a slave with a random address same as a search address or a slave of Physical Selection Mode.
VERIFY_SHORT_ADDRESS | 0x01B9 | #define DALI_VERIFY_SHORT_ADDRESS 0x01B9 //268 - Is the short address AAA AAA? | Special | 268 | 1011 1001 0AAA AAA1 |  | YES/NO | VERIFY SHORT ADDRESS |  | Is the short address AAA AAA?
QUERY_SHORT_ADDRESS | 0x01BB | #define DALI_QUERY_SHORT_ADDRESS 0x01BB //269 - What is the short address of the slaveNote 2being selected? | Special | 269 | 1011 1011 0000 0000 |  | 0AAA AAA1 | QUERY SHORT ADDRESS |  | What is the short address of the slaveNote 2being selected?
PHYSICAL_SELECTION | 0x01BD | #define DALI_PHYSICAL_SELECTION 0x01BD //270 not DALI-2 - Sets the slave to Physical Selection Mode and excludes the slave from the Compare process. (Excluding IEC62386-102ed2.0) (Command that exist only in IEC62386-102ed1.0, -207ed1.0) | Special | 270 | 1011 1101 0000 0000 |  | NO | PHYSICAL SELECTION | not DALI-2 | Sets the slave to Physical Selection Mode and excludes the slave from the Compare process. (Excluding IEC62386-102ed2.0) (Command that exist only in IEC62386-102ed1.0, -207ed1.0)
RESERVED271 | 0x01BF | #define DALI_RESERVED271 0x01BF //271 - [Reserved] | Special | 271 | 1011 1111 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
ENABLE_DEVICE_TYPE_X | 0x01C1 | #define DALI_ENABLE_DEVICE_TYPE_X 0x01C1 //272 - Adds the device XXXX (a special device). | Extending special | 272 | 1100 0001 XXXX XXXX |  | NO | ENABLE DEBICE TYPE X |  | Adds the device XXXX (a special device).
DATA_TRANSFER_REGISTER1 | 0x01C3 | #define DALI_DATA_TRANSFER_REGISTER1 0x01C3 //273 - Stores data XXXX into DTR1. | Extending special | 273 | 1100 0011 XXXX XXXX |  | NO | DATA TRANSFER REGISTER1 (DTR1) |  | Stores data XXXX into DTR1.
DATA_TRANSFER_REGISTER2 | 0x01C5 | #define DALI_DATA_TRANSFER_REGISTER2 0x01C5 //274 - Stores data XXXX into DTR2. | Extending special | 274 | 1100 0101 XXXX XXXX |  | NO | DATA TRANSFER REGISTER2 (DTR2) |  | Stores data XXXX into DTR2.
WRITE_MEMORY_LOCATION | 0x01C7 | #define DALI_WRITE_MEMORY_LOCATION 0x01C7 //275 - Write data into the specified address of the specified memory bank. (There is BW) (DTR(DTR0)：address, DTR1：memory bank number) | Extending special | 275 | 1100 0111 XXXX XXXX |  | reply | WRITE MEMORY LOCATION |  | Write data into the specified address of the specified memory bank. (There is BW) (DTR(DTR0)：address, DTR1：memory bank number)
WRITE_MEMORY_LOCATION_NO_REPLY | 0x01C9 | #define DALI_WRITE_MEMORY_LOCATION_NO_REPLY 0x01C9 //276 DALI-2 - Write data into the specified address of the specified memory bank. (There is no BW) (DTR(DTR0)：address, TR1：memory bank number) (Command that exist only in IEC62386-102ed2.0) | Extending special | 276 | 1100 1001 XXXX XXXX |  | NO | WRITE MEMORY LOCATION – NO REPLY | DALI-2 | Write data into the specified address of the specified memory bank. (There is no BW) (DTR(DTR0)：address, TR1：memory bank number) (Command that exist only in IEC62386-102ed2.0)
RESERVED277 | 0x01CB | #define DALI_RESERVED277 0x01CB //277 - [Reserved] | Extending special | 277 | 1100 1011 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED278 | 0x01CD | #define DALI_RESERVED278 0x01CD //278 - [Reserved] | Extending special | 278 | 1100 1101 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED279 | 0x01CF | #define DALI_RESERVED279 0x01CF //279 - [Reserved] | Extending special | 279 | 1100 1111 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED280 | 0x01D1 | #define DALI_RESERVED280 0x01D1 //280 - [Reserved] | Extending special | 280 | 1101 0001 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED281 | 0x01D3 | #define DALI_RESERVED281 0x01D3 //281 - [Reserved] | Extending special | 281 | 1101 0011 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED282 | 0x01D5 | #define DALI_RESERVED282 0x01D5 //282 - [Reserved] | Extending special | 282 | 1101 0101 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED283 | 0x01D7 | #define DALI_RESERVED283 0x01D7 //283 - [Reserved] | Extending special | 283 | 1101 0111 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED284 | 0x01D9 | #define DALI_RESERVED284 0x01D9 //284 - [Reserved] | Extending special | 284 | 1101 1001 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED285 | 0x01DB | #define DALI_RESERVED285 0x01DB //285 - [Reserved] | Extending special | 285 | 1101 1011 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED286 | 0x01DD | #define DALI_RESERVED286 0x01DD //286 - [Reserved] | Extending special | 286 | 1101 1101 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED287 | 0x01DF | #define DALI_RESERVED287 0x01DF //287 - [Reserved] | Extending special | 287 | 1101 1111 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED288 | 0x01E1 | #define DALI_RESERVED288 0x01E1 //288 - [Reserved] | Extending special | 288 | 1110 0001 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED289 | 0x01E3 | #define DALI_RESERVED289 0x01E3 //289 - [Reserved] | Extending special | 289 | 1110 0011 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED290 | 0x01E5 | #define DALI_RESERVED290 0x01E5 //290 - [Reserved] | Extending special | 290 | 1110 0101 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED291 | 0x01E7 | #define DALI_RESERVED291 0x01E7 //291 - [Reserved] | Extending special | 291 | 1110 0111 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED292 | 0x01E9 | #define DALI_RESERVED292 0x01E9 //292 - [Reserved] | Extending special | 292 | 1110 1001 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED293 | 0x01EB | #define DALI_RESERVED293 0x01EB //293 - [Reserved] | Extending special | 293 | 1110 1011 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED294 | 0x01ED | #define DALI_RESERVED294 0x01ED //294 - [Reserved] | Extending special | 294 | 1110 1101 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED295 | 0x01DF | #define DALI_RESERVED295 0x01DF //295 - [Reserved] | Extending special | 295 | 1110 1111 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED296 | 0x01F1 | #define DALI_RESERVED296 0x01F1 //296 - [Reserved] | Extending special | 296 | 1111 0001 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED297 | 0x01F3 | #define DALI_RESERVED297 0x01F3 //297 - [Reserved] | Extending special | 297 | 1111 0011 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED298 | 0x01F5 | #define DALI_RESERVED298 0x01F5 //298 - [Reserved] | Extending special | 298 | 1111 0101 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED299 | 0x01F7 | #define DALI_RESERVED299 0x01F7 //299 - [Reserved] | Extending special | 299 | 1111 0111 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED300 | 0x01F9 | #define DALI_RESERVED300 0x01F9 //300 - [Reserved] | Extending special | 300 | 1111 1001 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED301 | 0x01FB | #define DALI_RESERVED301 0x01FB //301 - [Reserved] | Extending special | 301 | 1111 1011 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
RESERVED302 | 0x01FD | #define DALI_RESERVED302 0x01FD //302 - [Reserved] | Extending special | 302 | 1111 1101 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 303 | 1010 0000 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 304 | 1010 0010 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 305 | 1010 0100 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 306 | 1010 0110 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 307 | 1010 1000 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 308 | 1010 1010 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 309 | 1010 1100 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 310 | 1010 1110 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 311 | 1011 0000 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 312 | 1011 0010 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 313 | 1011 0100 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 314 | 1011 0110 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 315 | 1011 1000 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 316 | 1011 1010 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 317 | 1011 1100 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 318 | 1011 1110 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 319 | 1100 0000 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 320 | 1100 0010 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 321 | 1100 0100 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 322 | 1100 0110 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 323 | 1100 1000 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 324 | 1100 1010 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 325 | 1100 1100 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 326 | 1100 1110 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 327 | 1101 0000 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 328 | 1101 0010 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 329 | 1101 0100 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 330 | 1101 0110 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 331 | 1101 1000 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 332 | 1101 1010 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 333 | 1101 1100 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 334 | 1101 1110 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 335 | 1110 0000 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 336 | 1110 0010 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 337 | 1110 0100 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 338 | 1110 0110 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 339 | 1110 1000 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 340 | 1110 1010 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 341 | 1110 1100 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 342 | 1110 1110 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 343 | 1111 0000 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 344 | 1111 0010 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 345 | 1111 0100 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 346 | 1111 0110 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 347 | 1111 1000 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 348 | 1111 1010 XXXX XXXX |  | NO | RESERVED |  | [Reserved]
|  |  | ??? | 349 | 1111 1100 XXXX XXXX |  | NO | RESERVED |  | [Reserved]

## Legend
Y: <0>Short address, <1>Group address/broadcast address A: Address bit 0SSS SSS1 = short address 100G GGG1 = group address 1111 1111 = broadcast X: Data DTR: Data Transfer Register YES: 1111 1111 NO: Without backward frame H,M,L: Search address
IEC62386-207 - Digital addressable lighting interface - Part 207: Particular requirements for control gear - LED modules (device type 6)